## Sheet1
Huawei R4850G2 Rectifier Module
Baud Rate 125kbps
Extended Frame
Command/Response | Addr | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | ID |  |  |  | Value
Request Data Frames: | 0x108040FE | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | Value Divisor
Receive Data: | 0x1081407F | 0x01 | 0x0E | 0x00 | 0x00 | 0x00 | 0x00 | 0x00 | 0x0A |  | Unknown frame
|  | 0x01 | 0x70 | 0x00 | 0x00 | Input Power |  |  |  | /1024
|  | 0x01 | 0x71 | 0x00 | 0x00 | Input Frequency |  |  |  | /1024
|  | 0x01 | 0x72 | 0x00 | 0x00 | Input Current |  |  |  | /1024
|  | 0x01 | 0x73 | 0x00 | 0x00 | Output Power |  |  |  | /1024
|  | 0x01 | 0x74 | 0x00 | 0x00 | Efficiency |  |  |  | /1024
|  | 0x01 | 0x75 | 0x00 | 0x00 | Output Voltage |  |  |  | /1024
|  | 0x01 | 0x76 | 0x00 | 0x00 | Output Current Max |  |  |  | /30
|  | 0x01 | 0x78 | 0x00 | 0x00 | Input Voltage |  |  |  | /1024
|  | 0x01 | 0x7F | 0x00 | 0x00 | Output Temperature |  |  |  | /1024
|  | 0x01 | 0x81 | 0x00 | 0x00 | Output Current |  |  |  | /1024 | This output current appears more accurate (on my single unit/sample)
|  | 0x01 | 0x82 | 0x00 | 0x00 | Output Current |  |  |  | /1024 | Not sure what this is?
|  | 0x01 | 0x83 | 0x00 | 0x10 | Unknown- normally zero
|  | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
|  | 0: ID; 4: Value | Value Multiplier
Set Data: | 0x108180FE | 0x01 | 0x00 | 0x00 | 0x00 | On-line Output Voltage |  |  |  | V * 1020 | Acceptable range 41.5 to 58.5V in 0.1V steps
|  | 0x01 | 0x01 | 0x00 | 0x00 | Off-line/Default Output Voltage |  |  |  | V * 1020 | Acceptable range 48 to 58.5V in 0.1V steps
|  | 0x01 | 0x02 | 0x00 | 0x00 | Overvoltage Protection? (Untested) |  |  |  | V * 1020 | Acceptable range 56.5 to 60.5V (as per datasheet)
|  | 0x01 | 0x03 | 0x00 | 0x00 | On-line Current Limit |  |  |  | A * 30 | Acceptable range 0 to 60A in 0.1A steps
|  | 0x01 | 0x04 | 0x00 | 0x00 | Off-line/Default Output Current Limit |  |  |  | A * 30 | Acceptable range 0 to 60A in 0.1A steps
Receive ACK: | 0x1081807E | 0: 0x01; 1: Mirrors transmitted frame | Successful
|  | 0: 0x21; 1: Mirrors transmitted frame | Error | Set value is likely out of range
The rectifier can operate in two states:
Off-line is when there is no CAN communication (i.e. standalone operation). This occurs on power-up or if CAN communication has timed-out (Orange LED slowly blinking).
On-line values are only valid when CAN communication is present (Orange LED not blinking). These values are volatile and reset to default on loss of CAN comms.
CAN communication time-out is approximately 60 seconds. i.e. if you stop sending valid CAN messages to the rectifier, the rectifier will switch to Off-line/Default values in approximately 60 seconds.